## Case Control Rqmts
Major Case Requirements (Controls) |  |  | Major Strategy Needed
1 | Case Temperature Control |  | N
| a | Defrost control(+ Different defrost types) | Y
|  | i)Defrost synchronization | Y
|  | Ii) Drain Operation | Y
| b | Superheat control | Y
| c | Control Fan | Y
2 | BMS Communication |  | Y
3 | Alarms & Failure Monitoring |  | Y
Minor Requirements
1 | Control lights |  | Y
2 | Monitor Fans |  | Y
3 | Antisweat Control |  | Y
4 | Case Cleaning |  | Y
5 | Dual Temperature operation |  | Y
6 | Door Switch Operation |  | Y

## Rev
Rev # | Author | Changes | Date Started | Jira Task #
v1.0 | Joshua Meduoye | Original Creation

## Input Output Reqmts
Compressor Protection
Discharge Air Temp Sensor &/ Return Air | [8 empty] | PWM EEV Control (Door*) Anti-condensate heaters*
MPX ONE MED -- AI = 6, AO=2, DI = 5, DO=4
Defrost Termination Temp Sensor | [8 empty] | Lights*
|  | DI 1 | DI 2 | DI 3 | DI 4 | DI 5
| AI 1 | Dollar Tree Architecture Diagram | [5 empty] | AO 1
| AI 2 | [6 empty] | AO 2
Coil Oulet Temperature | AI 3
AI 4
AI 5
AI 6
Coil Outlet Pressure
(Door)RH Sensor*
|  | DO1 | DO2 | DO3 | DO4
(Door) Cold Point Sensor*
Condensing Units | Drain Heater/Fan Fan* |  |  | Defrost Heater |  |  | Drain Heater*

## SYSTEM P Diagram
Major Function List
| NOISE 1: Piece to Piece |  | NOISE 2: Change Over Time |  | NOISE 3: Customer Usage |  | NOISE 4: External Environment |  | NOISE 5: System Interaction
| Piece to Piece |  | 2.Change Over Time | 3.Customer Usage |  | 4.External Environment |  | 5.System Interaction
Noise Factors | Sensor Location |  | Cleanliness of Case
| Sensor Tolerance |  | Caking of coil
|  |  | Coil oxidation | Improper temp sensor selection |  | Door Opening
Power Fluctuations
| Liquid flow variation |  | Actuator Drift | Improper expansion valve selection
| Actuator tolerance |  | Sensor Drift
Vapour flow variation
Low refrigerant
Inputs
Discharge Temp Sensor |  | Dollar Tree Case System P Diagram | [5 empty] | Desired Outputs
Defrost Termination Temp Sensor | [7 empty] | Efficient Refrigiration Control
Coil Outlet Temp Sensor* | [7 empty] | Pass Ashrae standards
Coil Outlet Pressure Sensor* | [7 empty] | Pass DOE Test for Energy
Compressor Protect Feedback* | [7 empty] | Efficient Defrost
ON/OFF Compressor | [7 empty] | Efficient Superheat control
Coil | [7 empty] | Reliability and Serviceability
Doors | [7 empty] | System Diagnostic Enable*
Mullion | [7 empty] | BMS System Compatiblilty*
Fans | [7 empty] | EOL & Functional Test*
EEV Valve*
Antisweat Heater
Lights & drivers
Case Power System
Klixons/Drain heater sensor
Condensing Unit Contactor
Relay for Defrost Heater
Fan/Drain Relay
Dew Point Controller (AEC)
Solid State Relays*
MPx One Controller | [7 empty] | Undesired Outputs
Evaporator pan | [7 empty] | Poor Refrigiration Control
Condensate Pump | [7 empty] | Failed Ashrae
Failed DOE
Inefficient Defrost
Inefficient Superheat control
Bad Service/Reliability
Non Diagnosible*
No Communication*
Unavailable func/EOL Test*
Control Factors | Discharge air temp setpoint
Coil outlet temp set point
Coil outlet pressure setpoint
Liquid pressure setpoint
Suction pressure setpoint
Drip time
Superheat setpoint
Pumpdown time

## FMEA
[13 empty] | Responsible Person | Actions Taken | Revised Rankings
Item | Component | Function | Potential Failure Mode | Potential Effect(s) of failure | SEVERITY | Potential Cause(s) of Failure | Occurrence | Current Design Controls(Prevention) | Current Design Controls(Detection) | Detection | RPN | Recommdended Action(s) | Target Completion Date | Effective Completion Date | Severity | Occurrence | Detection | RPN
1 | Discharge Temp Sensor | Main System for Temperature Control | Disconnected Discharge Temp Sensor
2 |  |  | Failed Discharge Temp Sensor
3 | Defrost Term Sensor | Used to ensure proper defrost completion | Disconnected Discharge Temp Sensor
4 |  |  | Failed Discharge Temp Sensor
5 | Coil Out Temp Sensor* | Used for Superheat calculation & comp protection logic | Disconnected Discharge Temp Sensor
6 |  |  | Failed Discharge Temp Sensor
7 | Coil Outlet Press Sensor* | Used for Superheat calculation & comp protection logic | Disconnected Discharge Press Sensor
8 |  |  | Failed Discharge Press Sensor
9 | Compressor Protection Feedback* | Feedback from Compressor fail | Unavailable Compressor Feedback
10 |  |  | Failed Compressor Feedback
11 | ON/OFF Compressor | Provide Refrigirant & Compress refrigirant | Compressor Not Delivering Compressed refrigirant
12 |  |  | Compressor Not Powered/Disconnected/Failed
13 |  |  | Compressor Leakage
14 | COIL | XX Heat Transfer XX Refrigirant Transport | Wrongly sized Coil (Width & Length & Circuiting)
15 |  |  | Coil Leakage
16 |  |  | Ice formation
17 | Doors | XX Improve Insulation XX Provides window to view product XX Provides Connectors for Lighting XX Allows efficient Temp Control | Bad gasket & inefficient seal
18 |  |  | Glass fogging
19 |  |  | No product illumination
20 |  |  | Failed mechanical ability to open or close doors
21 | Mullion | XX Structural Stability of the frame XX Provides housing for electrical wiring XX Provides housing for energy controller XX Provides houing for led driver | Broken, cracked Mullion
22 |  |  | Damage/Disconnect lights/energy controller
23
24
25 | Fans | xx - Provide heat distribution to product xx - Control case air flow xx - Used as a means for defrost (rvrs heat transfer) | Fan wrongly sized
26 |  |  | Fan disconected/ not working
27 |  |  | Fan blades broken
28 | EEV Valve* | xx - control refrigirant flow xx - Drop refrigirant pressure into coil xx- Stop refrigirant flow in end conditions | Not opening
29 |  |  | Not Closing
30 |  |  | Not working/ Disconnected/ Not operational
31 | Antisweat Heater* | xx- Eliminated condensation | Wrong specification
32 |  |  | Not connected/not operational
33 | Lights & drivers | xx Illumination of product | Not connected/ not Operational lights
34 |  |  | Not connected/ operational drivers
35 | Case Power System | xx - Provide power to all electrical comp.. | Loss of system power
36
37
38 | Klixon & Drain Heater sensor | xx - Drain heater overtemp protection xx - Ensure operator safety reduce likelyhood of burning | Wrongly calibrated klixon
39 |  |  | Incorrect program
40 |  |  | Not connected/ non operational
41 | Condensing Unit Contactor | xx-Turn condensing unit on and off | Wrong part #/wrong part installed
42 |  |  | Not connected properly/Trash inbetween contacts/contact won't close
43 |  |  | Contact stuck closed
44 |  |  | Failed contactor/mechanical failure
45 | Relay for Defrost Heaters | xx-Turn defrost heaters on and off | Wrong part #/wrong part installed
46 |  |  | Not connected properly/Trash inbetween contacts/contact won't close
47 |  |  | Contacts stuck closed
48 |  |  | Failed relay/mechanical failure
49 | Relay for Fan/Drain Heaters | xx-Turns fans and drain on and off xx- Drain heater logic | Wrong part #/wrong part installed
50 |  |  | Not connected properly/Trash inbetween contacts/contact won't close
51 |  |  | Contacts stuck closed
52 |  |  | Failed relay/mechanical failure
53 | Anthony Energy Controller (AEC) with rH sensor and temp sensor | xx- Control anti-sweat heaters based on dew point | Failed controller/not working
54 |  |  | Loose wiring/bad wiring connection - rH sensor, temp sensor, a/s heaters, power
55 |  |  | Calibration for dew point is not accurate/Not providing correct output
56 |  |  | rH sensor not functioning or installed correctly
57 |  |  | Temperature sensor not functioning or installed correctly
58 | Solid State Relay* | xx- Control the electronic valve for superheat | Wrong part #/wrong part installed
59 |  |  | Failed relay/electronic failure
60 |  |  | Optocoupler fails to turn output on/off
61 |  |  | Wrong specification for relay requirements (will not turn output on/off)
62 |  |  | Screw terminal connection failure/bad wiring connection to load or control side
63 | MpxOne Controller* | xx- Control refrigerated case xx- Fans, defrost heaters, CDU on/off, superheat*, drain heater* | Wrong part/wrong controller installed
64 |  |  | I/O damaged/not functioning
65 |  |  | Incorrect power supply*
66 |  |  | Incorrect program - Incorrect configuration/incorrect setpoints (user inputs)
67 |  |  | Incorrect software version
68 |  |  | BMS communication failure*
69 |  |  | Software bug
70 |  |  | Improper training
71 |  |  | Inadequate documentation
72 |  |  | Wrong design application
73 | Evaporator Pan | xx-Evaporates excess water drained from Evaporator coil | Bad wiring/wiring connection on evaporator pan side
74 |  |  | Bad float switch
75 |  |  | Bad/broken heater
76 |  |  | Wrongly sized component (wattage)
77 |  |  | Wrong electrical spec (120V vs. 208V)
78 |  |  | Blockage in float switch
79 | Condesate Pump+receptacle | xx- Pump excess water from evaporator coil to pan | Bad wiring/wiring connection on pump side
80 |  |  | Bad float switch
81 |  |  | Wrong component/part installed (shipped with case)
82 |  |  | Pump goes bad/stops working
83 |  |  | Clogging of drain line
84 |  |  | Blockage in float switch
85 |  |  | Bad/wrong wiring to receptacle
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212