## Revision History
REVISION HISTORY
Date | Name | Version | Comments
2020-02-05 | Joshua Meduoye | Rev 1 | Initial Creation, focused on formating
2020-04-08 | Joshua Meduoye | Rev 2 | Added Input Interface as discussed with Carel Team
2020-10-22 | Andrew Martin | Rev 3 | Updated Data Interface Output per release variable names

## Naming Conv
DFR Naming System for Magic Kingdom
| i. P_ - Powerdown (Keeps value across PowerCycles) | OM | Outut Manager
| ii. C_ - Calibratable (Read/Write) No change during runtime | IM | Input Manager
iii. V_ - Software Instantaneous Variable (Read Only)
No need if unit does not exist or NA
i. tms -time in sec
ii. tmm - time in mins
iii. tmh - time in hours
iv. pr -pressure in psi
v. prg -guage pressure
vi. tr - temperature in Fahrenheit
vii. trc - temperature in Celsius
viii. hz - frequency in Hertz
ix. pc - frequency in Hertz

## Data Interface Input
DFR Naming Nomenclature
|  | To Use a sensor, Status, Channel | * Auxilliary inputs are general purpose and are not used anywhere. This is based on customer application. Used mostly for Intercase/BMS communication
Type | DFR Name | Carel Name | Description | Unit | Data Type | Computation method | Min | Max | Initial Value | Resolution | Offset | Conversion Factor | Physical/COMM | Owner Name
AI | V_IM_trc_Air_Off | AnalogInputs.Fct.AirOff | Sensor 1: Air Off Temperature Sensor | Cel | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_trc_Air_On | AnalogInputs.Fct.AirOn | Sensor 1: Air Off Temperature Sensor Status | Cel | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_pc_Rh_Ambient | AnalogInputs.Fct.AmbientH | Ambient Relative Humidity Probe | % | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_trc_Ambient | AnalogInputs.Fct.AmbientT | Ambient Temperature | Celcius | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_Aux | AnalogInputs.Fct.Auxiliary | Auxilliary Temperature Probe | Celcius | Real | Remote | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_Aux2 | AnalogInputs.Fct.Auxiliary2 | Auxilliary Temperature Probe | Celcius | Real | Remote | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_trc_Coil | AnalogInputs.Fct.Defrost | Coil Temperature 1 for defrost | Celcius | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_trc_Coil2 | AnalogInputs.Fct.Defrost2 | COil Temperature 2 for defrost | Celcius | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_trc_DewPoint | AnalogInputs.Fct.DewPoint | Dew point Value (Inside Case?/Outside Case) | Celcius | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_bar_Evap | AnalogInputs.Fct.EvapP | Evaporator Outlet Pressure | bar | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_trc_Glass | AnalogInputs.Fct.GlassT | Glass Heater Temperature | Celcius | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
AI | V_IM_trc_Suction | AnalogInputs.Fct.SuctT | Suction Temperature | Celcius | Real | Local/Remote Sensor | 1e+38 | 1e+38 |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_Alarm_Flag | DigitalInputs.Fct.Alarm | Immediate External Alarm | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_Auxiliary_Flag | DigitalInputs.Fct.Auxiliary | Auxilliary DI | NA | BOOL | Remote | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_CallDfr_Flag | DigitalInputs.Fct.CallDfr | Defrost Request/Trigger | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_Clean_Flag | DigitalInputs.Fct.Clean | Clean Switch Input | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_Config_Flag | DigitalInputs.Fct.Config | Change Configuration | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_ContCycle_Flag | DigitalInputs.Fct.ContCycle | Continious Cycle Start/Stop | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_Curtain_Flag | DigitalInputs.Fct.Curtain | Curtain Switch | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_DefrostMirror_Flag | DigitalInputs.Fct.DefrostMirror | Defrostaligned with Digital Input Status | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_DelayedAl_Flag | DigitalInputs.Fct.DelayedAl | Delayed External Alarm | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_DoorOff_Flag | DigitalInputs.Fct.DoorOff | Door Status -Regulation OFF | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_DoorOn_Flag | DigitalInputs.Fct.DoorOn | Regulation ON | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_EnDfr_Flag | DigitalInputs.Fct.EnDfr | Defrost Enable/Trigger | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_GenFctAlrm_Flag | DigitalInputs.Fct.GenFctAlrm | Digital Input for Generic function Alarm | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_RemoteOff_Flag | DigitalInputs.Fct.RemoteOff | Remote ON/OFF Trigger | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_Standby_Flag | DigitalInputs.Fct.Standby | Stand by Switch | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel
DI | V_IM_Timed_Flag | DigitalInputs.Fct.Timed | Timed based digital input trigger | NA | BOOL | Local/Remote Sensor | NA | NA |  |  | As Configured |  | Physical | DFR/Carel

## Data Interface Ouput_CarelEdit
Global Switch | En_GlobalSwitch_Override
Type | DFR Name | Carel Physical Output Variable | MultiPlexer Switch (BOOL) | Carel Logic Variable | Custom Output Variable | DFR Final Name | Description | Unit | Data Type | Elements | Computation method | Min | Max | Initial Value | Resolution | Offset | Conversion Factor | Physical/Comm | Owner Name
Description: |  | Variable connected to Physical Output | To enable / disable HPX Logic | Result of Carel Logic | Result of HPX Logic
Global Switch
|  | En_GlobalSwitch_Override | [6 empty] | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
Type A - Controlled via Multiplexer
DO | V_OM_Alarm_Flag | DigitalOutputs.Fct.Alarm | En_AlarmOverwrite | OrAlrm | Custom_AlarmOutput | V_OM_Final_Alarm_Flag | Alarm Output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Auxiliary_Flag | DigitalOutputs.Fct.Auxiliary | En_AuxOutputOverwrite | AuxOn | Custom_AuxOutput | V_OM_Final_Auxiliary_Flag | Auxiliary Output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_MasterAuxiliary_Flag | DigitalOutputs.Fct.MasterAuxiliary | En_MstAuxOutputOverwrite | NetworkAux | Custom_MstAuxOutput | V_OM_Final_MasterAuxiliary_Flag | Master Auxiliary Output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Light_Flag | DigitalOutputs.Fct.Light | En_LightOverwrite | LightsOn | Custom_LightOutput | V_OM_Final_Light_Flag | Light Output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Fans_Flag | DigitalOutputs.Fct.Fans | En_FansOverwrite | FansOn | Custom_FansOutput | V_OM_Final_Fans_Flag | Fan Output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Timed_Flag | DigitalOutputs.Fct.Timed | En_TimedOutOverwrite | TimedOn | Custom_TimedOutput | V_OM_Final_Timed_Flag | Liquid Valve Output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_DrainHeat_Flag | DigitalOutputs.Fct.DrainHeat | En_DrainHeaterOverwrite | DfrStatus > DFR_IDLE (Logic) | Custom_DrainHeaterOutput | V_OM_Final_DrainHeat_Flag | Timed output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_RailHeaters_Flag | DigitalOutputs.Fct.RailHeaters | En_RailHeaterOverwrite | HeatersOut = 100 AND (Dout_Cfg.Arr[15].Ch > 0) (Logic) | Custom_RailHeaterOutput | V_OM_Final_RailHeaters_Flag | Rail heaater Output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_GenericStage1_Flag | DigitalOutputs.Fct.GenericStage1 | En_GenFctStageOverwrite | GenFctStages_Out[1] | Custom_GenFctStageOutput | V_OM_Final_GenericStage1_Flag | Generic Function Stage Output | NA | BOOL |  | Local | 0 | 1 | 0 |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_MasterLight_Flag | DigitalOutputs.Fct.MasterLight | En_MstLightOverwrite | NetworkLight | Custom_MstLightOutput | V_OM_Final_MasterLight_Flag | Master Light Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
AO | V_OM_Rails | AnalogOutputs.Fct.Rails |  | TO_REAL(HeatersOut) (Logic) |  | V_OM_Final_Rails | Rail Output | NA | REAL |  | Local | 0 | 100 | 0 | 0.1 | As Configured |  | Physical | DFR/Carel
AO | V_OM_GenericModul1 | AnalogOutputs.Fct.GenericModul1 | En_GenFctModulOverwrite | GenFctModul_Out[1] | Custom_GenFctModulOutput | V_OM_Final_GenericModul1 | Generic Function Module Output | NA | REAL |  | Local | 0 | 100 | 0 | 0.1
AO | V_OM_fans | AnalogOutputs.Fct.Fans |  | FansReq |  | V_OM_Final_fans | Fan Command Output | NA | REAL | -3.402e+38 | Local | 0 | 100 | 0 | 0.1 | As Configured |  | Physical | DFR/Carel
Type | DFR Name | Carel Name | Variable to Call Function | Description | Output Select(BOOL) | DFR Final Name | Description | Unit | Data Type | Elements | Computation method | Min | Max | Initial Value | Resolution | Offset | Conversion Factor | Physical/Comm | Owner Name
Type B - Controlled via Function Call
DO | V_OM_Solenoid_Flag | DigitalOutputs.Fct.Solenoid | CmdComp | 0: Forced Off 1: Automatic (temperatuer control to set the output) 2: Forced ON |  | V_OM_Final_Solenoid_Flag | Solenoid Output | NA | USINT |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Defrost_Flag | DigitalOutputs.Fct.Defrost | ManDfr | TRUE - Start Defrost. False - Stop Defrost |  | V_OM_Final_Defrost_Flag | Defrost Output for Coil1 | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Defrost2_Flag | DigitalOutputs.Fct.Defrost2 | - | Same as Defrost1, as long as parameter DOH > 0 |  | V_OM_Final_Defrost2_Flag | Defrost Output for Coil2 | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
Special | V_OM_Valve | AnalogOutputs.Fct.Valve | EnManExv | FALSE = Disable maual valve positioning TRUE = enable manual valve positioning |  | V_OM_Final_Valve | Valve Output | NA | USINT |  | Local | 0 | 480 | 0 | 1 | As Configured |  | Physical | DFR/Carel
|  |  | PosManExv | Manual valve position to set (0 steps to 480 steps)

## Data Interface Ouput_Original
Data
Type | DFR Name | Carel Name | Output Select(BOOL) | DFR Final Name | Description | Unit | Data Type | Elements | Computation method | Min | Max | Initial Value | Resolution | Offset | Conversion Factor | Physical/Comm | Owner Name
DO | V_OM_Solenoid_Flag | DigitalOutputs.Fct.Solenoid | V_Solenoid_Select_Flag | V_OM_Final_Solenoid_Flag | Solenoid Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Alarm_Flag | DigitalOutputs.Fct.Alarm | V_Alarm_Select_Flag | V_OM_Final_Alarm_Flag | Alarm Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Auxiliary_Flag | DigitalOutputs.Fct.Auxiliary | V_Auxiliary_Select_Flag | V_OM_Final_Auxiliary_Flag | Auxiliary Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_MasterAuxiliary_Flag | DigitalOutputs.Fct.MasterAuxiliary | V_MasterAuxiliary_Select_Flag | V_OM_Final_MasterAuxiliary_Flag | Master Auxiliary Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Light_Flag | DigitalOutputs.Fct.Light | V_Light_Select_Flag | V_OM_Final_Light_Flag | Light Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_MasterLight_Flag | DigitalOutputs.Fct.MasterLight | V_MasterLight_Select_Flag | V_OM_Final_MasterLight_Flag | Master Light Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Defrost_Flag | DigitalOutputs.Fct.Defrost | V_Defrost_Select_Flag | V_OM_Final_Defrost_Flag | Defrost Output for Coil1 | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Defrost2_Flag | DigitalOutputs.Fct.Defrost2 | V_Defrost2_Select_Flag | V_OM_Final_Defrost2_Flag | Defrost Output for Coil2 | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Fans_Flag | DigitalOutputs.Fct.Fans | V_Fans_Select_Flag | V_OM_Final_Fans_Flag | Fan Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_SuctVlv_Flag | DigitalOutputs.Fct.SuctVlv | V_SuctVlv_Select_Flag | V_OM_Final_SuctVlv_Flag | Suction Valve Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_EqualizVlv_Flag | DigitalOutputs.Fct.EqualizVlv | V_EqualizVlv_Select_Flag | V_OM_Final_EqualizVlv_Flag | Equalizer Valve Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Timed_Flag | DigitalOutputs.Fct.LiquidVlv | V_LiquidVlv_Select_Flag | V_OM_Final_Timed_Flag | Liquid Valve Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_DrainHeat_Flag | DigitalOutputs.Fct.Timed | V_Timed_Select_Flag | V_OM_Final_DrainHeat_Flag | Timed output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_Solenoid_Flag | DigitalOutputs.Fct.DrainHeat | V_DrainHeat_Select_Flag | V_OM_Final_Solenoid_Flag | Drain Heater Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_RailHeaters_Flag | DigitalOutputs.Fct.RailHeaters | V_RailHeaters_Select_Flag | V_OM_Final_RailHeaters_Flag | Rail heaater Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_GenericStage1_Flag | DigitalOutputs.Fct.GenericStage1 | V_GenericStage1_Select_Flag | V_OM_Final_GenericStage1_Flag | Generic Function Stage Output | NA | BOOL |  | Local | 0 | 1 |  |  | As Configured |  | Physical | DFR/Carel
DO | V_OM_fans | AnalogOutputs.Fct.Fans | V_Variablefan_Select_Flag | V_OM_Final_fans | Fan Command Output | NA | REAL |  | Local | -3.402e+38 | 3.402e+38 |  |  | As Configured |  | Physical | DFR/Carel
AO | V_OM_Valve | AnalogOutputs.Fct.Valve | V_Variablefan_Select_Flag | V_OM_Final_Valve | Valve Output | NA | REAL |  | Local | -3.402e+38 | 3.402e+38 |  |  | As Configured |  | Physical | DFR/Carel
AO | V_OM_Rails | AnalogOutputs.Fct.Rails | V_Rails_Select_Flag | V_OM_Final_Rails | Rail Output | NA | REAL |  | Local | -3.402e+38 | 3.402e+38 |  |  | As Configured |  | Physical | DFR/Carel
AO | V_OM_GenericModul1 | AnalogOutputs.Fct.GenericModul1 | V_GenericModul1_Select_Flag | V_OM_Final_GenericModul1 | Generic Function Module Output | NA | REAL |  | Local | -3.402e+38 | 3.402e+38

## Alarms Interface Input
All Alarms always set the status for the sensor to a Non-Valid State
Carel Alarm Names | Alarm Code | Description | Owner | Debounce | Count
Alarms.Al.Al_HiTemp[i].Info.Trigger |  | If High temp is detected then trigger alarms. Ensure the system having the alarms pertaining to clean operation are false that time (i=1,2) | CAREL | Alarm delay variable = '120' min
Alarms.Al.Al_LowTemp[i].Info.Trigger |  | If Low temp detected then trigger alarms. Ensure the system having the alarms pertaining to clean operation are false that time (i=1,2) | CAREL
Al_HA.Info.Trigger |  | Trigger alarms associated with 'HACCP HA' instances | CAREL | HACCP alarm delay='0 min(initial val)'
Alarms.Al.Al_HA.Info.Trigger |  | Trigger alarms associated with 'HACCP HA' instances within some bounds | CAREL
Al_HF.Info.Trigger |  | Trigger alarms associated with 'HACCP HF' instances | CAREL | HACCP alarm delay > 0
Alarms.Al.Al_HF.Info.Trigger |  | Trigger alarms associated with 'HACCP HF' instances | CAREL
Alarms.Arr[i].Info.Trigger |  | Wizard Inhibition Alarms | CAREL
Alarms.Al.AlExtDin.Info.Trigger |  | Trigger alarms associated with Digital Inputs | CAREL
Alarms.Al.Al_MA.Info.Trigger |  | Trigger alarms for slave devices when master is not polling | CAREL | 60 secs
Alarms.Al.Al_u[i].Info.Trigger |  | Trigger alarms for looping the Communication error with Slave (only on Master) alarms | CAREL
Alarms.Al.Al_GHI_1.Info.Trigger |  | Generic Alarms | CAREL
Alarms.Al.Al_GLO_1.Info.Trigger |  | Generic Alarms | CAREL
Alarms.Al.Warn_TrialVer.Info.Trigger |  | Generic alarms for Warnings | CAREL
Alarms.Al.AlDelayExtDin.Info.Trigger |  | Trigger alarms associated with Digital Inputs after TON delay time | CAREL | AlDinDelay='0' min (initial val)
Alarms.Al.Al_n[i].Info.Trigger |  | Loop the Alarm on unit 1 to 9 in the network | CAREL
Alarms.Al.Al_RTC.Info.Trigger |  | Real Time clock fault | CAREL
Alarms.Al.Al_PrbBroken[i].Info.Trigger |  | Broken Probe error alarms | CAREL
Alarms.Al.Al_PrbBroken[Ain_Cfg.Arr[i].Ch].Info.Trigger |  | Broken Probe error alarms for AIN function block | CAREL
Alarms.Al.Warn_SuctP_Prb.Info.Trigger |  | Suction Pressure Probe not connected warning alarms | CAREL
Al_SerialInputs[i].Trigger |  | Serial Inputs alarm trigger | CAREL | 20 minutes
Alarms.Al.Al_Reg.Info.Trigger |  | Regulation alarms trigger | CAREL
Alarms.Al.Warn_Door.Info.Trigger |  | Door ON and OFF warning alarm triggers | CAREL
Alarms.Al.Al_Door.Info.Trigger |  | Door On alarm triggers | CAREL | 30 Minutes (Min - 1 min, Max - 240 min)
Alarms.Al.Status_Standby.Info.Trigger |  | Standby alarms | CAREL | StByTout- config variable for standby operation
Alarms.Al.Status_Clean.Info.Trigger |  | Clean status alarm triggers | CAREL | CleanTout - config variable for clean operation
Alarms.Al.Al_LSA.Info.Trigger |  | EXV alarms | CAREL
Alarms.Al.Al_LSH.Info.Trigger |  | EXV alarms | CAREL
Alarms.Al.Al_MOP.Info.Trigger |  | EXV alarms | CAREL
Alarms.Al.DfrTout1.Info.Trigger |  | Defrost alarms | CAREL
Alarms.Al.DfrTout2.Info.Trigger |  | Defrost alarms | CAREL
Alarms.Al.Al_MOP.Info.Trigger |  | EXV alarms | CAREL
Alarms.Al.AL_DA1_EVDmini.Info.Trigger |  | EXV alarms S1 probe | CAREL
Alarms.Al.AL_DA2_EVDmini.Info.Trigger |  | EXV alarms S2 probe | CAREL
Alarms.Al.Al_DEE_EVDmini.Info.Trigger |  | EEPROM EVD alarms | CAREL
Alarms.Al.Al_DE5_EVDmini.Info.Trigger |  | EVD emergency closing alarms | CAREL
Alarms.Al.Warn_EVD_Fw.Info.Trigger |  | EVD Warning alarms | CAREL
Alarms.Al.Al_bLO.Info.Trigger |  | EXV alarms | CAREL | 30 sec
Alarms.Al.Al_Edc.Info.Trigger |  | EXV alarms | CAREL
AinGrCfg.Trigger |  | Ain Config error trigger in IO Manager | CAREL
AinCfg[i].Trigger |  | Ain Triggers in IO Manager | CAREL
DinCfg[i].Trigger |  | Din Triggers in IO Manager | CAREL
AoutCfg[i].Trigger |  | Aout Triggers in IO Manager | CAREL
DoutCfg[i].Trigger |  | Dout Triggers in IO Manager | CAREL

## Help With Hooks
To be Provided by Carel
a | Inputs |  |  |  | Output and status to be provided
a | Air curtain Speed target | (** Initial Creation: 3/5/2020 Joshua Meduoye Component Level B Dover Food and Retail Defrost Input Management ****** This component is focused on software development on getting inputs into the system There are 2 major parts 1. Features Features contain software focused on creating new functionality 2. Diagnostics Diagnostics are focused on failure detection and troubleshooting ****** **) (** +++++++++++++++++++++++++++Analog Input Sensors Processing+++++++++++++++++++++++++ Sensor 1: Air Off Temperature Sensor - V_trc_Air_Off & V_trc_Air_Off_Status Sensor 2: Defrost Temperature Sensor - V_trc_Defrost & V_trc_Defrost_Status Sensor 3: Air On Temperature Sensor - V_trc_Air_On & V_trc_Air_On_Status Sensor 4: Suction Temperature Sensor - V_trc_Suction & V_trc_Suction_Status Sensor 5: Ambient Temperature Probe - V_trc_Ambient & V_trc_Ambient_Status Sensor 6: Ambient Humidity Sensor - V_pc_Rh_Ambient & V_pc_Rh_Ambient_Status Sensor 7: Drain Temperature Sensor - V_trc_Drain & V_trc_Drain_Status Sensor 8: Case R Humidity Sensor - V_pc_Rh_Case & V_pc_Rh_Case_Status Sensor 9: Glass Temperature Sensor - V_trc_Glass & V_trc_Glass_Status Sensor 10: Evaporator Temperature Sensor - V_trc_Evap & V_trc_Evap_Status Sensor 11: Coil Outlet Pressure - V_prg_Coil_Out & V_prg_Coil_Out_Status Sensor 12: Frame Temp Sensor - V_trc_Frame & V_trc_Frame_Status **) (** +++++++++++++++++++++Digital Input Sensors Processing++++++++++++++++++++++ Sensor 1: Door Switch - V_pt_Door_Open & V_pt_Door_Open_Status Sensor 2: Clean Switch - V_pt_Case_Clean & V_pt_Case_Clean_Status Sensor 3: Occupancy Sensor - V_pt_Occ_Detect & V_pt_Occ_Detect_Status Sensor 4: Service Switch - V_pt_Service & V_pt_Service_Status Sensor 5: Multi-purpose Input Functions - V_bt_DIn_Trigger **) (** Sensor Fail Working Mechanism DFR_Sensor_Status Data_Valid = 0 //means there is a sensor without any errors giving accurate values Data_Valid_Remote = -1 //Means that this value is recieving input from a remote device Data_Error_Model_High = -2 //means that the sensor is bad but there is a model developed supplying high accuracy values Data_Error_Model_Low = -3 //means that the sensor is bad but there is a model that gives low confidence values Data_Error_Default = -4 //means that the sensor has an issue but there is an default acceptable value that meets system expectations Data_Error_Suspect = -5 //Means Sensor is connected but is suspected to be broadcasting wrong values Data_Error_Timeout = -6 //Means that a sensor is possibly not connected **) (** ++++++++++++++++++++++++++++++++++++Analog Input Processing++++++++++++++++++++++++++++++++++++ **) (** Analog Input Sensors Processing Sensor 1: Air Off Temperature Sensor - V_trc_Air_Off & V_trc_Air_Off_Status **) (** Analog Input Sensors Processing Sensor 2: Defrost Temperature Sensor - V_trc_Defrost & V_trc_Defrost_Status **) (** Analog Input Sensors Processing Sensor 3: Air On Temperature Sensor - V_trc_Air_On & V_trc_Air_On_Status **) (** Analog Input Sensors Processing Sensor 4: Suction Temperature Sensor - V_trc_Suction & V_trc_Suction_Status **) (** Analog Input Sensors Processing Sensor 5: Ambient Temperature Probe - V_trc_Ambient & V_trc_Ambient_Status **) (** Analog Input Sensors Processing Sensor 6: Ambient Humidity Sensor - V_pc_Rh_Ambient & V_pc_Rh_Ambient_Status **) (** Analog Input Sensors Processing Sensor 7: Drain Temperature Sensor - V_trc_Drain & V_trc_Drain_Status **) (** Analog Input Sensors Processing Sensor 8: Case R Humidity Sensor - V_pc_Rh_Case & V_pc_Rh_Case_Status **) (** Analog Input Sensors Processing Sensor 9: Glass Temperature Sensor - V_trc_Glass & V_trc_Glass_Status **) (** Analog Input Sensors Processing Sensor 10: Evaporator Temperature Sensor - V_trc_Evap & V_trc_Evap_Status **) (** Analog Input Sensors Processing Sensor 11: Coil Outlet Pressure - V_prg_Coil_Out & V_prg_Coil_Out_Status **) (** Analog Input Sensors Processing Sensor 12: Frame Temp Sensor - V_trc_Frame & V_trc_Frame_Status **) (** ++++++++++++++++++++++++++++++++++++Digital Input Processing++++++++++++++++++++++++++++++++++++ **) | On The Ouput Side, we would simply like to know that status of each of these outputs and how to update the status when it changes. E.g. If we want to turn off the lightsm out process would be to look at the light status first, and if it is OFF, we do nothing. Else we turn it off, and we would also need to update the status to ensure your software knows its turned off too
a | Fan count Array
a | Fan Status Array
Yes | Curr Discharge air temperature value
Yes | Defrost status
Fan type Array
Yes | Door switch status Array
Yes | Defrost Request Mode
Yes | Humidity value |  |  |  | V_OM_Solenoid_Flag
| Power status Array |  |  |  | V_OM_Alarm_Flag
Yes (Fan Status) | Defrost Fan request status |  |  |  | V_OM_Auxiliary_Flag
Yes | Cleaning Status |  |  |  | V_OM_MasterAuxiliary_Flag
Yes (If Available) | Curr Return Air temperature |  |  |  | V_OM_Light_Flag
| Discharge Air Status |  |  |  | V_OM_MasterLight_Flag
Yes (Sens Status) | return Air Status |  |  |  | V_OM_Defrost_Flag
Yes (Sens Status) | Humidity status |  |  |  | V_OM_Defrost2_Flag
V_OM_Fans_Flag
V_OM_SuctVlv_Flag
V_OM_EqualizVlv_Flag
V_OM_Timed_Flag
V_OM_DrainHeat_Flag
V_OM_Solenoid_Flag
V_OM_RailHeaters_Flag
V_OM_GenericStage1_Flag
V_OM_fans
V_OM_Valve
V_OM_Rails
V_OM_GenericModul1
Meets our requirement
Yes ( Door Status) | Door Value |  | Path A | Path B
Yes (Door Sens Avail) | Door Status |  | HPX can write directly to the output | Recommended to activate via Function Calls
Yes | Humidity
Yes | Humidity sensor status |  | Alarm Output | Clean Output
Yes | Return Air temperature |  | Auxiliary Output | Standby Output
Yes | Return Air temperature Status |  | Master Auxiliary Output | Remote ON/OFF
Yes | Discharge Air Temperature |  | Light Output | Door switch (stopping the regulation)
Yes | Discharge Air Temperature Status |  | Master Light Output | Shared solenoid network Output
| Air flow speed |  | Fan Output | Solenoid Output
Yes | Fan status |  | Timed output | Defrost Output for Coil1
Yes | Ambient temp |  | Drain Heater Output | Defrost Output for Coil2
Yes | Ambient Temp status |  | Rail heaater Output | Suction Valve Output
| Door frame temperature |  | Generic Function Stage Output | Equalizer Valve Output
| Frame heating status |  | Fan Command Output | Liquid Valve Output
| Glass heating status |  | Rail Output | Valve Output (only manual mode without Carel's safeties)
| Rail Heating status |  | Generic Function Module Output
| Mass of Coil frost* |  |  | Modbus Fan Output*
Yes | Door Switch Value Array
Yes | Ambient temperature value
Frame temperature value
Yes | Humidity value
Yes | Cleaning status
Power status
Yes | Ambient temperature status
Frame temperature status
Yes | Humidity status
Door Switch Status Array
Inputs
Time Since Last Defrost
Defrost request mode
Left pipe chase temperature value if required
yes | Defrost status
Power status
Left pipe chase temperature status
yes | Cleaning status
yes | Drainhtrstatus
Yes | Fan Status
Yes | Refrigiration Status
Inputs
Time
Yes( Light Status) | PIR/Occupancy/Camera Light trigger
PIR/Occupancy/Camera Status
Power status
Light output avail | Light switch status
Light Request Interface*(Need more discussion)
Yes( Light Status) | Light switch
Estimated mass of frost
Frost Monitor Root Cause
Frost Accumulation rate
Yes (If available) | Dew Point
Bunkered Coil Suspect
Yes | Setpoint
Defrost Criteria
>Time Interval Btw defrost
>Maximum Defrost time
>Termination temperature
>Minimum Defrost Time
>Drip Time
> Fan Behavior
> Defrost Type
>Defrost Timebands
Coil Temperature Value
Coil Temperature Status
Yes | Coil heater Status
Yes | Power Status
Yes | >Electrical Heater status
Yes | Fan Status
Yes | Cleaning Status
Yes(EEV Value) | EEV Status
Yes | LLSV Status
Hot gas solenoid status
Time Interval
Defrost Request Mode
Yes | > Remote Defrost
yes(Refrigiration Status) | > Refrigiration Off only defrost
> Failed Defrost Refrost
> Forced Defrost
> System Protection Defrost
> Product Defrost Request
Yes | >BMS Defrost
>Opportunistic defrost(Dani Load Shedding)
Current Time
Current Time Status
Yes | Refrigerant type
Door Open Rate
Door Status
Air Speed
yes | Ambient Temp and Status
yes | Discharge Air Temp & Status
Yes | Case Setpoint
Yes | Relative Hunidity (outside Case)
Yes | Case Setpoint
Yes | Defrost Status
Yes | Superheat actual
Yes | Refrigeration Status
yes | Refrigerant Type
Yes | Case Suction Pressure
Refrigiration Efficiency
Relative Weight of frost*
Inputs
Yes | Defrost status
Yes | Fan status
yes | Coil outlet Temperature Value
Yes | Coil outlet Pressure value
Yes | Discharge air temp value
Yes | Electrical Heater status
Yes | Cleaning Status
Yes | EEV Status
Yes | LLSV Status
Yes | Hot gas solenoid status
Yes | Door switch status
Yes | Defrost Request
Yes | Liquid pressure
yes | Suction pressure
Power status
Temperature Control Mode
Pumpdown mode
Yes | Refrigerant type
Yes | Coil outlet Temperature Value
Yes | Coil outlet Pressure value
Yes | Discharge air temp value
Yes | Electrical Heater status

## Alarms Interface Output & Enbl
Alarm Name | Alarm Code | Desciption | Owner | Debounce | Count

## DFRScheduling
Service Name | Description | Scheduling rate(ms) | Priority

## CarelScheduling
Service Name | Description | Scheduling rate(ms) | Priority

## Carel Special Functions
Function Name | Description | Function Prototype | Inputs | Input data type | Output | Output Datatype