## Architecture Diagram Mpx Basic
Compressor Protection
Discharge Air Temp Sensor
AI = 3, DI = 2, DO = 4
Defrost Termination Temp Sensor
|  | DI 1 | DI 2
| AI 1 | Dollar Tree Architecture Diagram
AI 2
AI 3
1. Can we eliminate the Klixons
2. Can we elimnate the relays
|  | DO1 | DO2 | DO3 | DO4
Condensing Units | Drain Heaters |  |  | Defrost Heater |  | Fan

## Architecture Diagram Mpx Med
Compressor Protection
Discharge Air Temp Sensor | [8 empty] | PWM EEV Control (Door*) Anti-condensate heaters*
MPX ONE MED -- AI = 6, AO=2, DI = 5, DO=4
Defrost Termination Temp Sensor | [8 empty] | Lights*
|  | DI 1 | DI 2 | DI 3 | DI 4 | DI 5
| AI 1 | Dollar Tree Architecture Diagram | [5 empty] | AO 1
| AI 2 | [6 empty] | AO 2
Coil Oulet Temperature | AI 3
AI 4
AI 5
AI 6
Coil Outlet Pressure
(Door)RH Sensor*
|  | DO1 | DO2 | DO3 | DO4
(Door) Cold Point Sensor*
Condensing Units | Drain Heater/Fan Fan* |  |  | Defrost Heater |  |  | Drain Heater*

## SYSTEM P Diagram
Major Function List
| NOISE 1: Piece to Piece |  | NOISE 2: Change Over Time |  | NOISE 3: Customer Usage |  | NOISE 4: External Environment |  | NOISE 5: System Interaction
| Piece to Piece |  | 2.Change Over Time | 3.Customer Usage |  | 4.External Environment |  | 5.System Interaction
Noise Factors | Sensor Location |  | Cleanliness of Case
| Sensor Tolerance |  | Caking of coil
|  |  | Coil oxidation | Improper temp sensor selection |  | Door Opening
Power Fluctuations
| Liquid flow variation |  | Actuator Drift | Improper expansion valve selection
| Actuator tolerance |  | Sensor Drift
Vapour flow variation
Low refrigerant
Inputs
Discharge Temp Sensor |  | Dollar Tree Case System P Diagram | [5 empty] | Desired Outputs
Defrost Termination Temp Sensor | [7 empty] | Efficient Refrigiration Control
Coil Outlet Temp Sensor* | [7 empty] | Pass Ashrae standards
Coil Outlet Pressure Sensor* | [7 empty] | Pass DOE Test for Energy
Compressor Protect Feedback* | [7 empty] | Efficient Defrost
ON/OFF Compressor | [7 empty] | Efficient Superheat control
Coil | [7 empty] | Reliability and Serviceability
Doors | [7 empty] | System Diagnostic Enable*
Mullion | [7 empty] | BMS System Compatiblilty*
Fans | [7 empty] | EOL & Functional Test*
EEV Valve*
Antisweat Heater
Lights & drivers
Case Power System
Klixons/Drain heater sensor
Condensing Unit Contactor
Relay for Defrost Heater
Fan/Drain Relay
Dew Point Controller (AEC)
Solid State Relays*
MPx One Controller | [7 empty] | Undesired Outputs
Evaporator pan | [7 empty] | Poor Refrigiration Control
Condensate Pump | [7 empty] | Failed Ashrae
Failed DOE
Inefficient Defrost
Inefficient Superheat control
Bad Service/Reliability
Non Diagnosible*
No Communication*
Unavailable func/EOL Test*
Control Factors | Discharge air temp setpoint
Coil outlet temp set point
Coil outlet pressure setpoint
Liquid pressure setpoint
Suction pressure setpoint
Drip time
Superheat setpoint
Pumpdown time

## FMEA
[13 empty] | Responsible Person | Actions Taken | Revised Rankings
Item | Component | Function | Potential Failure Mode | Potential Effect(s) of failure | SEVERITY | Potential Cause(s) of Failure | Occurrence | Current Design Controls(Prevention) | Current Design Controls(Detection) | Detection | RPN | Recommdended Action(s) | Target Completion Date | Effective Completion Date | Severity | Occurrence | Detection | RPN
1 | Discharge Temp Sensor | Main System for Temperature Control | Disconnected Discharge Temp Sensor | [7 empty] | 0
2 |  |  | Failed Discharge Temp Sensor | [7 empty] | 0
3 | Defrost Term Sensor | Used to ensure proper defrost completion | Disconnected Discharge Temp Sensor | [7 empty] | 0
4 |  |  | Failed Discharge Temp Sensor | [7 empty] | 0
5 | Coil Out Temp Sensor* | Used for Superheat calculation & comp protection logic | Disconnected Discharge Temp Sensor | [7 empty] | 0 |  | Proneet Banerjee 11/06/2020 | Proneet Banerjee 11/06/2020
6 |  |  | Failed Discharge Temp Sensor | [7 empty] | 0
7 | Coil Outlet Press Sensor* | Used for Superheat calculation & comp protection logic | Disconnected Discharge Press Sensor | [7 empty] | 0 |  | Proneet Banerjee 11/06/2020 | Proneet Banerjee 11/06/2020
8 |  |  | Failed Discharge Press Sensor | [7 empty] | 0
9 | Compressor Protection Feedback* | Feedback from Compressor fail | Unavailable Compressor Feedback | Currently not available | [6 empty] | 0
10 |  |  | Failed Compressor Feedback | Currently not available | [6 empty] | 0
11 | ON/OFF Compressor | Provide Refrigirant & Compress refrigirant | Compressor Not Delivering Compressed refrigirant | Case not maintaining temp | 10 | compressor internally damaged,wrong sized compressor | 5 | None | None | 10 | 500 | Use a current sensor to measure the amps of compressor, *contactor with auxilary contact to input on controller | Harsha Mathur 11/06/2020 | Harsha Mathur 11/06/2020
12 |  |  | Compressor Not Powered/Disconnected/Failed | Case will not run | 10 | Power feed not connected,loose wire off of contactor,Power from main feed not supplied | 5 | None | None | 10 | 500 | Use a current sensor to measure main feed, *contactor with auxilary contact to input on controller
13 |  |  | Compressor Leakage | Over a period of time it will trip on low pressure | 10 | Braze joints have leak, broken fittings, flare nuts not tighten, factory weld leaks | 5 | Low pressure alarm | Low pressure alarm | 10 | 500 | Algorithm that can detect deterioration of pressure over time - rate in drop of pressure over time - currently R448a, subcooling calculation to detect leak (more consisten)
14 | Evaporator Coil | XX Heat Transfer XX Refrigirant Transport | Wrongly sized Coil (Width & Length & Circuiting) | Will not reach case setpoint | 10 | Engineering defect - wrongly sized, production set the wrong coil | 2 | high temperature alarm | high temperature alarm | 6 | 120 | None at this time
15 |  |  | Coil Leakage | Will not maintain temperature | 10 | crack in copper tubing,braze joint leaking,exspanion valve leaking | 5 | Low pressure alarm | Low pressure alarm | 10 | 500 | Algorithm that can detect deterioration of pressure over time, or the rise in discharge air temperature over time excluding defrost
16 |  |  | Ice formation | causes premature frost | 5 | [5 empty] | 0
17 | Doors | XX Improve Insulation XX Provides window to view product XX Provides Connectors for Lighting XX Allows efficient Temp Control | Bad gasket & inefficient seal | insuffient seal, or disturbed air flow | 6 | gasket door seal installed improperly,case installed under air vent in store area | 7 | None | None | 6 | 252 | Algorithm that can detect deterioration of discharge air temp rising plus a drop in coil temperature
18 |  |  | Glass fogging | premature frost on coil and product | 6 | gasket door seal installed improperly, design problem | 7 | None | None | 6 | 252 | Algorithm with higher than normal humidity inside of the case
19 |  |  | No product illumination | Can not see product thru door | 9 | seal around frame not installed properly, no heat in the door | 5 | None | None | 8 | 360 | Algorithm with higher than normal humidity inside of the case?
20 |  |  | Failed mechanical ability to open or close doors | Damage/Disconnect lights/energy controller | 6 | bad wiring or component | 5 | None | None | 2 | 60 | CT on the lighting circuit
21 | Mullion | XX Structural Stability of the frame XX Provides housing for electrical wiring XX Provides housing for energy controller XX Provides houing for led driver | Broken, cracked Mullion | Case door will not open or close | 6 | mechanical parts not installed correctly | 1 | None | None | 5 | 30 | none needed
22 |  |  | Damage/Disconnect lights/energy controller | Frost on coil | 6 | Broken during installation,broken during transport | 5 | None | None | 2 | 60
23 | [10 empty] | 0
24 | [10 empty] | 0
25 | Fans | xx - Provide heat distribution to product xx - Control case air flow xx - Used as a means for defrost (rvrs heat transfer) | Fan wrongly sized | [7 empty] | 0
26 |  |  | Fan disconected/ not working | premature frost on coil, low superheat, loss of compressor | 8 | Installed wrong fan motor, or engineering error | 2 | low temperature/low pressure alarm | low temperature/low pressure alarm | 8 | 128 | Algorithm that can detect deterioration of discharge air temp rising plus a drop in coil temperature, low superheat alarm
27 |  |  | Fan blades broken | premature frost on coil,low superheat, loss of compressor | 8 | production wiring miss, manufacturer defect |  | None | None |  | 0 | Algorithm that can detect deterioration of discharge air temp rising plus a drop in coil temperature, *sensor location needs to be considered*
28 | EEV Valve* | xx - control refrigirant flow xx - Drop refrigirant pressure into coil xx- Stop refrigirant flow in end conditions | Not opening | premature frost on coil | 8 | fans installed incorrectly | 3 | None | None |  | 0 | Algorithm that can detect deterioration of discharge air temp rising plus a drop in coil temperature | Harsha Mathur 11/06/2020 | Harsha Mathur 11/06/2020
29 |  |  | Not Closing | [7 empty] | 0
30 |  |  | Not working/ Disconnected/ Not operational | [7 empty] | 0
31 | Antisweat Heater* | xx- Eliminated condensation | Wrong specification | [7 empty] | 0
32 |  |  | Not connected/not operational | [7 empty] | 0
33 | Lights & drivers | xx Illumination of product | Not connected/ not Operational lights | No illumination inside the case | 2 | Faulty lights | 2 | Correct part number for lights are chosen | None | 5 | 20 | Possible use of CT's for lighting ckts | Harsha Mathur 13/10/2020 | Harsha Mathur 09/10/2020 | Same as before
34 |  |  | Not connected/ operational drivers |  | 2 | Faulty drivers | 2 | Correct part number of drivers are chosen | None | 5 | 20
35 | Case Power System | xx - Provide power to all electrical comp.. | Low or High Voltage to the Case | 1. Refrigeration will get affected due to low/no power 2. Damage to display case components | 10 | Faulty elec. Components, overcurrent, overvoltage, low voltage etc. | 5 | 1. Proper wiring according to standards and electrical schematic. 2. Correct part number for different electrical components are chosen. | None | 10 | 500 | 1. Energy Monitoring can tell about low voltage/Over voltage 2. Alarms associated with low/high voltage/current
38 | Klixon & Drain Heater sensor | xx - Drain heater overtemp protection xx - Ensure operator safety reduce likelyhood of burning | Wrongly calibrated klixon | [7 empty] | 0
39 |  |  | Incorrect program | [7 empty] | 0
40 |  |  | Not connected/ non operational | [7 empty] | 0
41 | Condensing Unit Contactor | xx-Turn condensing unit on and off | Wrong part #/wrong part installed | [7 empty] | 0
42 |  |  | Not connected properly/Trash inbetween contacts/contact won't close | [7 empty] | 0
43 |  |  | Contact stuck closed | [7 empty] | 0
44 |  |  | Failed contactor/mechanical failure | [7 empty] | 0
45 | Relay for Defrost Heaters | xx-Turn defrost heaters on and off | Wrong part #/wrong part installed | Defrost action may or may not happen when required and performance will get compromised | 7 | Human Error/Repository not maintained not properly | 2 | Part Numbers should be revalidated before procurement/Installation | No detection | 6 | 84
46 |  |  | Not connected properly/Trash inbetween contacts/contact won't close |  | 7 | Incorrect Wiring procedures/Physical Wear or Contamination /Failure due to change in enviroment exceeding specified technical value of the relay | 3 | Avoid Contamination of Contacts/Contacts should be cleaned properly before fitting to the relay base | No detection | 6 | 126 | 1. Any algorithm that detects stuck closed contacts by monitoring the temp Variation(Preferred) 2. Provision of Relay Feedback to detect failure in case of spare IO's
47 |  |  | Contacts stuck closed |  | 7 | High Inrush Current or High Voltage Spikes | 3 | Avoid High Inrush Currents,Sustained Currents ,Voltage Spikes and Inductive Loads/If contact surface is oxidized then it should be cleaned properly | No detection | 6 | 126 | 1. Any algorithm that detects stuck closed contacts by monitoring the temp Variation(Preferred) 2. Provision of Relay Feedback to detect failure in case of spare IO's
48 |  |  | Failed relay/mechanical failure |  | 7 | Mechanical Relay Contains Spring which loose resiliency with time/During Maintanence the coil insulation may get damaged due to tool's bruising | 3 | During Maintanence Coil Spring should be replaced /Wear and tear due to tools should be avoided | No detection | 6 | 126 | 1. Any algorithm that detects stuck closed contacts by monitoring the temp Variation(Preferred) 2. Provision of Relay Feedback to detect failure in case of spare IO's
49 | Relay for Fan/Drain Heaters | xx-Turns fans and drain on and off xx- Drain heater logic | Wrong part #/wrong part installed | Fan/Drain Heater action may or may not happen when required and performance will get compromised | 7 | Human Error/Repository not maintained not properly | 2 | Part Numbers should be revalidated before procurement/Installation | No detection | 6 | 84
50 |  |  | Not connected properly/Trash inbetween contacts/contact won't close |  | 7 | Incorrect Wiring procedures/Physical Wear or Contamination /Failure due to change in enviroment exceeding specified technical value of the relay | 3 | Avoid Contamination of Contacts/Contacts should be cleaned properly before fitting to the relay base | No detection | 6 | 126 | 1. Any algorithm that detects stuck closed contacts by monitoring the temp Variation(Preferred) 2. Provision of Relay Feedback to detect failure in case of spare IO's
51 |  |  | Contacts stuck closed |  | 7 | High Inrush Current or High Voltage Spikes | 3 | Avoid High Inrush Currents,Sustained Currents ,Voltage Spikes and Inductive Loads/If contact surface is oxidized then it should be cleaned properly | No detection | 6 | 126 | 1. Any algorithm that detects stuck closed contacts by monitoring the temp Variation(Preferred) 2. Provision of Relay Feedback to detect failure in case of spare IO's
52 |  |  | Failed relay/mechanical failure |  | 7 | Mechanical Relay Contains Spring which loose resiliency with time/During Maintanence the coil insulation may get damaged due to tool's bruising | 3 | During Maintanence Coil Spring should be replaced /Wear and tear due to tools should be avoided | No detection | 6 | 126 | 1. Any algorithm that detects stuck closed contacts by monitoring the temp Variation(Preferred) 2. Provision of Relay Feedback to detect failure in case of spare IO's
53 | Anthony Energy Controller (AEC) with rH sensor and temp sensor | xx- Control anti-sweat heaters based on dew point | Failed controller/not working | [7 empty] | 0
54 |  |  | Loose wiring/bad wiring connection - rH sensor, temp sensor, a/s heaters, power | [7 empty] | 0
55 |  |  | Calibration for dew point is not accurate/Not providing correct output | [7 empty] | 0
56 |  |  | rH sensor not functioning or installed correctly | [7 empty] | 0
57 |  |  | Temperature sensor not functioning or installed correctly | [7 empty] | 0
58 | Solid State Relay* | xx- Control the electronic valve for superheat | Wrong part #/wrong part installed | Superheat Regulation may or may not happen when required and performance will get compromised | 7 | Human Error/Repository not maintained not properly | 2 | Part Numbers should be revalidated before procurement/Installation | No detection | 6 | 84
59 |  |  | Failed relay/electronic failure |  | 7 | High Voltage Transient Spikes and Noise | 3 | Select the correct SSR relay for the application | No detection | 6 | 126 | 1. Any algorithm that detects stuck closed contacts by monitoring the Superheat Variation(Preferred) 2. Provision of Relay Feedback to detect failure in case of spare IO's
60 |  |  | Optocoupler fails to turn output on/off |  | 7 | High Voltage Transient Spikes and Noise/Wrong SSR selection | 3 | Select the correct SSR relay for the application | No detection | 6 | 126 | 1. Endurance Test Certificate should be provided by Supplier 2. Any algorithm that detects stuck closed contacts by monitoring the Superheat Variation(Preferred) 3. Provision of Relay Feedback to detect failure in case of spare IO's
61 |  |  | Wrong specification for relay requirements (will not turn output on/off) |  | 7 | Human Error and Incorrect Estimations | 3 | Revalidate the estimation before sending the requirements | No detection | 6 | 126
62 |  |  | Screw terminal connection failure/bad wiring connection to load or control side |  | 4 | Loose Wiring or Soldering of Wire/ Defect in Screw Terminals | 3 | Follow the right wiring practices | No detection | 6 | 72 | 1. Any algorithm that detects stuck closed contacts by monitoring the Superheat Variation(Preferred) 2. Provision of Relay Feedback to detect failure in case of spare IO's
63 | MpxOne Controller* | xx- Control refrigerated case xx- Fans, defrost heaters, CDU on/off, superheat*, drain heater* | Wrong part/wrong controller installed
64 |  |  | I/O damaged/not functioning
65 |  |  | Incorrect power supply*
66 |  |  | Incorrect program - Incorrect configuration/incorrect setpoints (user inputs)
67 |  |  | Incorrect software version
68 |  |  | BMS communication failure*
69 |  |  | Software bug
70 |  |  | Improper training
71 |  |  | Inadequate documentation
72 |  |  | Wrong design application
73 | Evaporator Pan | xx-Evaporates excess water drained from Evaporator coil | Bad wiring/wiring connection on evaporator pan side | Evap Pan does not work at all. Water will overflow. | 8 | 1. Evap pan received from manufacturer with defect |  | None | None |  |  | 1. Have manufacturer do quality test on Evap pans
74 | [5 empty] | 2. Evap pan not wired properly | [5 empty] | 2. Recommend if we are still using evap pans that come not prewired that we only offer prewired pans. Evap pans that come with plug prewired.
75 | [5 empty] | 3. Receptacle for evap pan not wired correctly | [5 empty] | 3. Verify correct wiring of receptacle during case electrical check.
76 |  |  | Bad float switch | 2 outcomes. 1) Float switch does not trip and heater does not turn on. Water will overflow. | 1) 8 | Bad float switch, float switch fails, too much junk in the water that it builds up on float |  | None | None |  |  | None
77 |  |  |  | 2) Float switch is stuck in the on position and heater won’t turn off. | 2) 10
78 |  |  | Bad/broken heater | Water would overflow | 8 | Heater is bad from vendor or breaks over time |  | None | None |  |  | Verify heater turns on during electrical check
79 | Condesate Pump+receptacle | xx- Pump excess water from evaporator coil to pan | Bad wiring/wiring connection on pump side | Pump does not work at all. Water will overflow. Or back up into case. | 9 | Pump received from manufacturer with defect |  | None | None |  |  | Have manufacturer do quality test on pump
80 |  |  | Bad float switch | 1) Float switch does not trip and water will overflow at pump or backup into case | 6 | Bad float switch, float switch fails, too much junk in the water causing float switch to malfunction, or float switch is too sensitive a trips sporadically. |  | None | None |  |  | Possibly have a redundant float switch in case of failure.
81 |  |  |  | 2) Float switch is stuck in the on position or float switch is too sensitive and goes off sporadically.
82 |  |  | Wrong component/part installed (shipped with case) | Depends what is incorrect. If just another pump is installed and it can still handle the amount of water, there is not issue. If that is not the situation water could overflow as pump cannot keep up with water from case. | 2-5 | Error on order, incorrect sales pick, or wrong evap pan installed on the line |  | None | None |  |  | We need correct parts on orders. Verify what is installed matched what is on the order.
83 |  |  | Pump goes bad/stops working | Pump does not work at all. Water will overflow. Or back up into case. | 9 | This is usually related to too much build up on the pump from debris in the water. This prevents the pump from working properly or makes the pump fail. |  | None | None |  |  | Make sure that customer is using strainer in the case to keep large debris out of the pump. Also clean pump periodically to prevent buildup.
84 |  |  | Clogging of drain line | Assuming this is between case and the pump. This will cause water to build up in the case. For low temp cases the water will freeze and slowly build up until case stops working. | 9 | Usually related to a kink in the hose or debris in the drain line from case. |  | None | None |  |  | Ensure that the case goes out without screws etc in the case that can fall down the drain. Make sure drain strainer is installed and that customer is using strainer. Periodically clean out case using clean out port on drain piping and clean out drain line if needed
85 |  |  | Blockage in float switch | Float switch will either completely not work or not operate properly | 6 | This would occur with a defective float switch or if the float switch gets too much build up on it from debris in the water. |  | None | None |  |  | Possibly have a redundant float switch in case of failure.
86 |  |  | Hose gets kinked | Water overflows or backs up into case | 8 |  | 8 | None | None |  |  | I think another solution to look at is to see if the evap pan or even the pump pan/container have overflow ports. This would protect against damaging electrical components on the evap pan and pump. Right now we do not connect the overflow port to anything. For top mount cases we might want to consider adding a drain hose to this overflow port and at least have to water drain down to the floor and not on top of the case in the event of overflow. That would keep other electrical items on the top of the case from getting wet. Howere, this will then be another spot that could get clogged.
87 |  |  | Pump vertical requirement exceeded when palced on top of case | Water does not get pumped all the way to the top |  |  |  | None | None
88 |  |  | Hose not secured to the evap pan |  |  |  |  | None | None
89 |  |  | Air gets in the hose | Air keeps additional water from being pumped to the pan |  | Evap pan is not positioned correctely and allows both water and air into the hose |  | None | None
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212

## Sheet5
Rev # | Author | Changes | Date Started | Jira Task #
v1.0 | Joshua Meduoye | Original Creation